## Sheet1
193450-000 NKU Residence Hall
1-30-2020 Bid Drawing Review Comments/Questions
Item # | Drawing # |  | Comment | Response
2/3/20 Questions Issued Prior to 2/6/20 Documents
1 | S110 | THP | Typical structural note 3 refrences S110 which isn't included | [THP] Note has been clarified. | 2020-02-06
2 | A701 | MN | door 100A head detail refers to 13/A523 which illustrates a steel beam on Structural. Detail 13/S401 on S102 doesn't included the steel beam shown on architectural. | Changed head detail reference for door 100A to 13/A523 SIM. Note: "NO BEAM @ SIM." added to detail 13/A523. | 2020-02-06
3 | A701 | LAS | General hardware note B says to undercut unit entry doors 3/4". Isn't the unit entry rated and must seal up tight? | Note has been revised. | 2020-02-06
4 | A701 | MN | 135A says detail 5/A720 which doesn't match the floor plan double door | reference changed to 5/A721 | 2020-02-06
5 | A701 | LAS / MN | doors 110 and 112 (cased openings no door) have hardware set 10 identified. -Is the HM frame a NKU requirement? Seems wastefull | Door frames delted. Openigns moved | 2020-02-06
6 | A701/A812 | LAS | Bedroom 2 need it's own entry door designation (in lieu of B1) | B1 is not a door number designation, but rather a door type - all bedrooms are Type B or B1 (for ADA). The Unit and RM Apartment schedules are set up to display each type of door instead of each indivdiual door. For example, both bedrooms in the RM apartment comply with ADA, and are threfore a Type B1 door. The schedule then outlines the requirements for a Type B1 door. | 2020-02-06
7 | A701 | MN | Missing hardware sets for B1, C1, F | Hardware sets for these door types have been added | 2020-02-06
8 | A701 | MN | Is note 8 requesting a 90min rating correct? | Yes. As indicated on Sheet A122 Doors 158, 161 and 162 are located in 2 hour bearing walls. These doors need to be 90 minut rated in order to keep the rating continuous. | 2020-02-06
9 | A530 | MN | RTU screen are not designed.Is it on another page? | The RTU screen is a premanufactured system that is simply attached to the RTU's. See CityScapes website: www.cityscapesinc.com | 2020-02-06
10 | A901 | LAS | PC-1 & SC-1 (polished and sealed concrete) are not identified in the key notes on the finished legend. This also typical of 800's enlarged units finishes | Duplicate comment. This has been corrected. | 2020-02-06
11 | A822 | LAS | incomplete. Maybe this was revised/included on Monday? | Was in-progress at the time of printing - was included in Monday's revised set. | 2020-02-06
2/12/20 Questions From Bidders and Drawings/Specification Issued 2/2/20 |  |  |  |  | Date Competed
1 | A721 | MN | Please confirm the location where detail 19 is to be utilized. | This is the storefront window for the study on the 5th floor. However, since it is the same as Elevation 08/A721 we have removed it from the sheet. | 2020-02-13
2 | Plumbing Questions | CMTA | 1.) Will trap seals in lieu of trap primers be an acceptable alternate? | No. Trap primers required for all FD-3 type floor drains. | 2020-02-14
3 | Plumbing Questions | CMTA | 2.) Will Meg Press fittings in lieu of threaded/Welded gas line be accepted? | No – engineer and owner rejected | 2020-02-14
4 | Plumbing Questions | CMTA | 3.)Will CPVC in lieu of Pex or copper for the domestic system be acceptble? | No – engineer and owner rejected | 2020-02-14
5 | Plumbing Questions | CMTA | 4.) Is a deduct meter for the irrigation system required? If so please proivde a specification section. | Refer to Sheet P200 | 2020-02-14
6 | Plumbing Questions | CMTA | 5.) Should there be a backflow and meter for the geothermal fill in the mechanical room? If so please provide a specification section. | CMTA will add reduced pressure backflow preventer and fill for the goethermal system - Will include in final addendum. | 2020-02-18
7 | Plumbing Questions | CMTA | 6.) Please provide a specification for the gas regulator at the generator | CMTA will porivde gas regulator spec - Will include in final addendum. | 2020-02-18
8 | Plumbing Questions | CMTA | 7.) Please confirm Note P25 on P101 should read 2.5 inch line and not 2.5 pound service. | 2.5# service to the generator, 2" pipe size. It gets regulated down at generator. Refer to detail on sheet P001 and routing on sheet P100. | 2020-02-14
9 | Spec's | LAS | 1.) Section 081416 – Flush Wood Doors – Spec States Residential Unit Entry Doors – We are assuming these are Maple Doors or should these be the MDO doors referenced in spec at Unit Door Entry A and RM Manager Apt Entry Doors? | The RM Manager Apt Entry door is a HM door since it is an exterior door (see Door Schedule). The Residential Unit Entry doors will be factory finished, wood veneer doors as outlined the specification. Doors 106 and 114 can be painted HM. Door schedule will be revised accordingly. | 2020-02-13
10 | Spec's | LAS | 2.) Tag 106 and Tag 114 – Are these to be considered 081416 – Flush Wood Doors? Are these Maple or MDO? | See response to Item 9 above | 2020-02-13
11 | Window Shades | LAS | Spec's include horizontal louver blinds and window shade systems. A few of the drawing pages say to refer to the finish schedule for window treatments which are not included. | As outlined in the Specifications, windows in residential units will receive horizontal louver blinds. Additional direction is needed from NKU on roller shade/ blind location in Common Areas. | 2020-02-13
12 | Spec - Fire Proofing | MN | I find a spec listed on the Table of Contents for 07 81 16 Cementitious Fireproofing but there is not an actual spec. | Spec section will be added in Addendum #1 | 2020-02-14
13 | Dimising Walls | MN | Please provide a detail for the head condition of the dimising walls that includes the exposed epicor decking and the fire caulked drywall partition that will be exposed. | See Details 1B and 1C on Sheet G007. These details will be revised to indicate that all firestop sealants to be painted. Detail 1B' will be revised to indiate that it is only acceptable when hidden above a ceiling. | 2020-02-13
14 | Ridge Mineral Wool Insulation | MN | Please confirm the type of insulation that is required behind the Fiber Cement Panels that will create or maintain the rainscreen system. | Details indicate "Rigid mineral Wool Insulation" for all continuous insulation above the lowest floor level. See Section 07 21 00 Paragraph 2.02. | 2020-02-12
15 | SP | MN | Substitution Request: Add Fiberglass Windows as an Alternate to Aluminum Windows. I was wondering if we would be permitted to submit as a voluntary alternate utilizing our Impervia Fiberglass. We are currently replacing windows at Schneider Hall at UC with this type of window. The architect wanted something that was thermally better than thermally broken aluminum and we showed him our fiberglass product and they loved it. This is the product we would like to propose. Would this be alright or do we need to get in contact with the architects? Please let me know at your earliest convenience. | Contractor to provide a completed Substitution Request form along with all required supporting documentation. See below | 2020-02-18
16 | DR | Kleingers | Revise grade along Kenton. No new sidewalk. | Revisions to be included in Addendum #1 | 2020-02-13
17 | SP | MN | Substitution Request: Add Metal Products, Inc. (MPI) to Section 08 11 00 | Substitution request approved. | 2020-02-13
18 | SP | MN | Substitution Request: Add Canton Elevators to Section 14 24 23 | Add Canton Elevators to Section 14 24 23 | 2020-02-13
19 | SP | MN | Door Hardware - verify | Revisions to be included in Addendum #2 | 2020-02-18
20 | SP | MN | Substitution Request: Boyd Aluminum to Section 08 51 13 | NKU to respond - see below | 2020-02-18
21 | Fire Protection |  | Specification Section 210100 Part 4 - Who is responsible for what equipment? | BC-02 - Site utility contractor will provide all exterior piping including meter pit and components at the meter pit and extend piping to just above finished floor in Fire Pump Room. BC-12 - Fire Protection contractor to provide all interior piping and equipment from point of connection at stubbed up piping. | 2020-02-13
2/13/20 Questions From Bidders and Drawings/Specification Issued 2/2/20 |  |  |  |  | Date Competed
22 | Spec's | LAS/MN | 062000 Finish Carpentry is incomplete listed in the TOC, but is not included in the project manual. | This specification section should have been removed from the project manual. | 2020-02-13
23 | Spec's | LAS/MN | Division 11 Equipment is blank. Where should bidders go to find items like hoods and dishwashers? | General Note 19 on sheet A811 outlines equipment requirements. We will revise the note accordingly | 2020-02-13
24 | Spec's | Kleingers | Termite Treatment 31 31 16 was deleted from the updated spec's. Was this intentional? | See below | 2020-02-18
25 | Spec's | Kleingers | The previous manual included 32 31 31 Trash Dumpster Enclosure and the current manual does not. | See below | 2020-02-18
26 | Spec's | MN | Would MN please verify sections listed on the TOC have been included in the Manual to eliminate additional Subcontractor questions? | Section 06 20 00 has been removed from the TOC - see item 22 above. | 2020-02-14
27 | Spec 08 14 33 | LAS | 081433 – Stile & Rail Doors - This specification is calling out for Masonite Cendura Series, West End Collection, Berkley – This is door with a 5 line design, however, the plans are showing flush doors – Please advise if the doors to the typical interior unit doors is to be this Design or flush | Section 081433 is for the ADD ALTERNATE to provide hollow core doors at the interior residential unit doors. Base bid should be solid core, flush wood doors as indicated in the drawings. Section 081433 should be used in conjunction with the ADD ALTERNATE. | 2020-02-13
28 | A811 & A850 | LAS | On A811 states quartz tops for the kitchen countertop. Should bidders also assume that the transaction top shown in details 11/A850, 10/A850, and elevation on 6/A811 are also quartz or should is be solid surface per comments on A900 finish schedule. | Finish Legend - Basis of Design on A900 indicates for Quartz to be used at Common Area Kitchen. This includes all counter surfaces in the kitchen. The transaction top included in details 11/A850, 10/A850 and elevation 6/A811 are all included as a part of the Common Area Kitchen Countertop reference. | 2020-02-13
29 | C500, A501, S301, S302 | Kleingers / MN / THP | Please coordinate where the interior underslab foundation drainage is supposed exit the foundations and where it will tie-into the storm system. | Revisions to be included in Addendum #1 | 2020-02-13
30 | A811 & A850 | LAS | Section 12 36 00 includes solid surface window stools but these can not be found on A500's or A700's pages. Which openings receive solid surface window stools? The only window stool I can find is 7/A820 that occurs in Vestibule 135V and it call out solid surface countertop. | Solid Surface window stools will not be used on this project. Delete 1.01, C and 3.04 from Section 12 36 00. Detail 7/A820 is correct to include a solid surface cap on the wall of the Vestibule on the Common Area side of the wall, which continues across to cap the partial height wall that extends out from the Vestibule. Refer to 1/A120. | 2020-02-13
2/13/20 Questions From Bidders and Drawings/Specification Issued 2/2/20-Sent 2/13 7pm |  |  |  |  | Date Competed
31 | Spec's | MN | Section 01 25 00 Substitution Procedures is not included in the TOC | Section 01 25 00 Substitution Procedures added to the TOC in Addendum #1 | 2020-02-13
32 | Spec's | MN / THP | 1.) Section 04 00 00 Part 1 A.4&.5, Section 05 12 00 1.2D.5, Section 05 30 00, and 05 51 13 all reference section 05 50 00-not included or should be another Section. | Revised Sections 04 00 00, 05 12 00, 05 30 00, 05 40 00, 05 51 13 & 1073 16 | 2020-02-14
33 | Spec's | THP | 2.) Section 05 12 00 Part 1.2D.2 reference 04 20 00 Unit Masonry I.L.O. 04 00 00 | Revised Sections 03 30 00, 05 12 00, & 05 40 00 | 2020-02-14
34 | Spec's | THP | 3.) Section 05 12 00 1.2D.5 references section 09 90 00 Painting I.L.O 09 91 00 Paintings and Coatings | Revised Sections 05 12 00, & 07 46 46 | 2020-02-14
35 | Section 07 11 13 | MN | Part 1 1.01 A states that the exterior of foundation walls and other areas. It appear the elevator pit is covered under Section 07 10 00. It would make sense for 5' wall that separates the ground floor elevation change to receive something but the drawing details do not indicate where. Details 1&2 on A522 call for 07 27 26 and 06 16 00. Please provide a drawing that will clarify where Bituminous Damproofing is required to be installed. | plans and details revised to clarify locations of fluid applied air barrier, waterproofing and dampproofing. | 2020-02-13
36 | 2/A522 | MN | The bottom note in this detail appears to be pointing at the fluid applied membrane and air-barrier but is calling out 06 16 00 Air and Water resistant sheathing board. Is this correct? | detail revised to clarify locations of fluid applied air barrier: on CMU only. | 2020-02-13
37 | Section 12 48 13 | LAS | Spec 124813 Entrance Floor Mats, please confirm thickness as ¼ or 7/16 | Proved thickness of 7/16" | 2020-02-14
ITEMS FOR ADDENDUM #2
2/17/20 Questions From Bidders and Drawings/Specification for ADDENDUM #2 |  |  |  |  | Date Competed
1 | Plumbing Questions | CMTA | 5.) Should there be a backflow and meter for the geothermal fill in the mechanical room? If so please provide a specification section. | CMTA will add reduced pressure backflow preventer and fill for the goethermal system - Will include in final addendum. | 2020-02-18
2 | Plumbing Questions | CMTA | 6.) Please provide a specification for the gas regulator at the generator | CMTA will porivde gas regulator spec - Will include in final addendum. | 2020-02-18
3 | SP | MN | Substitution Request: Add Fiberglass Windows as an Alternate to Aluminum Windows. I was wondering if we would be permitted to submit as a voluntary alternate utilizing our Impervia Fiberglass. We are currently replacing windows at Schneider Hall at UC with this type of window. The architect wanted something that was thermally better than thermally broken aluminum and we showed him our fiberglass product and they loved it. This is the product we would like to propose. Would this be alright or do we need to get in contact with the architects? Please let me know at your earliest convenience. | Contractor has not provided a completed Substitution Request form along with all required supporting documentation. Substitution denied. | 2020-02-18
4 | SP | MN | Door Hardware - verify | Revisions to be included in Addendum #2 | 2020-02-18
5 | SP | MN | Substitution Request: Boyd Aluminum to Section 08 51 13 | Approved. Revision to be included in Addendum #2 | 2020-02-17
6 | Spec's | Kleingers | Termite Treatment 31 31 16 was deleted from the updated spec's. Was this intentional? | Yes | 2020-02-18
7 | Spec's | Kleingers | The previous manual included 32 31 31 Trash Dumpster Enclosure and the current manual does not. | Yes | 2020-02-18
8 | 10 14 00 | LAS | Substitution Request: Fastsigns | Approved. Revision to be included in Addendum #2 | 2020-02-17
9 | 26 50 00 | CMTA | Substitution Request: Lighting | Approved. Revision to be included in Addendum #2 | 2020-02-17
10 | MEP | CMTA | Regarding the Airflow Dampers (AFD) scheduled for this project, following are the remarks included on the equipment schedules: REMARKS: 1. PROVIDE WITH FACTORY 24 VAC EXTERNALLY MOUNTED ACTUATOR WITH TRANSFORMER. 2. PROVIDE WITH FACTORY PRESSURE TRANSDUCER. 3. CONTROLS CONTRACTOR TO PROVIDE FILED MOUNTED CONTROLLER. REFER TO CONTROLS SPECIFICATION SECTION 250400 FOR DETAIL. 4. PROVIDE ACCESS DOOR IN DUCT PER SPECIFICATIONS UPSTREAM OF UNIT FOR MAINTENANCE ACCESS. 5. AFD'S SHALL BE PROVIDED AS SHOWN ON THE 5TH, 4TH AND 3RD FLOOR OUTSIDE AIR FOR A TOTAL OF 6 AFD'S. We are working with the local Greenheck rep to coordinate control work for these units. Question is, the schedule remark #3 states “REFER TO CONTROLS SPECIFICATION SECTION 250400 FOR DETAIL”. We do not see a reference to these units in the sequence of operation. Not sure what the function of the field mounted controller referred to in remark #3 will be. Unsure of the temperature control contractor scope as relates to these units. Please clarify. | A control sequence has been added for the Air Flow Dampers in Addendum #2 | 2020-02-18
11 | A701 | MN | Please provide A701 Door Schedule information for openings 21821 and 21822, listed but missing schedule info; | Theses doors were inadvertantly included in the door shedule. They have bee removed. | 2020-02-17
12 | A701 | MN | A701 Door Schedule lists a 3670 opening on level 2, however the ID and schedule info is missing, please provide; | This was revised in Addendum #1 | 2020-02-17
13 | Door Details | MN | Are HM Frames in Masonry Walls to be welded or knock down; | See Section 08 11 00 Paragraph 2.05 Steel Frames - all frames to be fully welded. | 2020-02-18
14 | Fire Extinguishers | LAS | Please confirm the FEC locations shown on G002 are the only required extinguishers, and 5lb extinguishers are not required in each unit; | Confirmed - extinguishers are not required in each unit. | 2020-02-18
15 | Bath Accessories | LAS | Please clarify unit Toilet Accessory requirements, only framed mirrors, towel rods, and grab bars are shown on the drawings | All accessories in the public restrooms are shown on both the plans and elevations on sheets A813 – A815. All residential unit accessories are outlined in the specifications: toilet paper holders and shower rods should also be included in addition to what’s shown on the drawings. Drawings will be revised to include notes for this | 2020-02-18
16 | Electrical | CMTA | The one-line shows a 175kW NG Gen-Set, however the engineer includes a keynote for upsize to 300kW. Please confirm, is a 300kw power output required? | Drawing note requires a 175kW generator with an upsized 300kW alternator. | 2020-02-18
17 | Finishes | LAS | What are the basis of design colors for the plastic laminate, solid surface & quartz colors? Should "standard" colors be assumed? | The finish schedule/ legend on Sheet A900 includes BOD colors for Quartz and for plastic laminate for the common area kitchen. Laminate and solid surface for the RM apartment and for the residential units have not been finalized yet with NKU. Assume standard laminate colors for the RM apartment and Morning Ice (9204CE) or equal for the solid surface counters. Final colors will be approved by NKU | 2020-02-18
18 | Mock-up | MN | Please supply drawing or derscribe the extents of materials required to furnish the project mock-up panel listed in Section 01 43 39 | Mock-up wall elevation added to Sheet A301 in Addendum #2 | 2020-02-18
19 | Section 08 41 13 | MN | It seems that (2) aluminum framing specification have been supplied (08 41 13 & 08 40 00), which one should be utilized? | 08 41 13 is for Exterior Aluminum Storefront & 08 40 00 is for Interior Aluminum Doors and Frames. | 2020-02-18
20 | Storefront | LAS | Interior Storefronts are noted as having a 4" depth and also as having a 4-1/2" depth, which will be required? | 4" depth is typical for the systems outlined in the specifications. | 2020-02-18
21 | Storefront | MN | Aluminum storefronts are noted as having an anodized finish and also as having a painted finish, which will be required or will (2) finishes be required? | Interior storefronts will have a clear anodized finish | 2020-02-18
22 | Bathroom Mirror | LAS | Are Framed/unframed mirrors to be supplied by BC-15? | This scope is listed in BC-01 on note 29. d. | 2020-02-18
23 | Section 08 41 13 | MN | Section 08 41 13-9,3.02-D.1 states to anchor storefront sill with a continuous aluminum anchor, are you describing a sub sill extrusion anchoring condition? | Yes. | 2020-02-18
24 | Pre fab shower/tub | LAS/ CMTA | Will the prefabricated showers/tubs include intrugual grab bars or will these be added after the units have been installed? | units have been specified to have integral grab bars. | 2020-02-18
25 | Blocking Requirements | LAS | Please clarify blocking needs for prefab shower/tub units, if any. | See BC-01 26.a. which state the perimeter of shower walls shall require blocking. Any mounting flange on the pre-fabricated units will require wood blocking. Additionally, blocking for Division 10 items, specified shower accessories, and ADA accessories require blocking. | 2020-02-18
26 | Section 10 28 00 | MN | The specfications call for Xlerator Hand Dryers and BP-01 item #31 calls for Dyson Airblade. Please confirm which is correct? | Dyson Airblade shall be provided and installed by BC-01 Specifications to be revised in Addendum #2 | 2020-02-18
27 | Restroom Shelf | LAS | A813 110W shows a “Shelf, see specs” adjacent to the hand dryer, corresponding to BC-01 item #33 “Provide 10x24 book shelf…” please provide a spec for this shelf; | This shelf was added in Section 10 28 00, paragraph 2.04, Item B. A detail will be provided with a future addendum | 2020-02-18
28 | A924 | LAS | 1/A924 note states “provide blocking in wall for dedication plaque…” please clarify this blocking requirement | NKU requested blocking be included in the wall for their dedication plaque. This item will need to be coordinated with NKU, Moody Nolan and LAS. | 2020-02-18
29 | G002 | LAS | Unit types listed on Code Sheet G002 do not match Floor Plans A101 – A105. Please advise which we are to follow for counts on Unit types | Floor plans and table listed on G002 have been revised to match. Refer to revised drawings. | 2020-02-18
30 | Site Logistics Plan | Messer | Please provide a size and loading requirement for the hoist access ramp and loading dock; | Provide a 22’x30’x6” thick 4000psi concrete slab with #4 rebar 3’ O.C. | 2020-02-18
31 | Roofing Questions | Messer | It is difficult to determine from the Roof Level Structural Plan on sheet S106 but I am assuming the entire roof system will require tapered insulation. Is that correct? | The structural roof decking is flat. Please find A106 and supporting notes and details to determine the extent of the tapered insulation. | 2020-02-18
32 | Roofing Questions | MN | I cannot find a proper detail where the wall of Stair 2 meets the main roof level. Will metal counterflashing be required along this wall and if so what will the configuration be | This detail would be similar to Detail 7/A702 | 2020-02-18
33 | LV401 | J&A | Sheet LV 401 Note 6 states Security Contractor to provide and install all video surveillance cameras,mounts and wiring | 33: Owner to provide camera hardware. Contractor to install and cable. See attached for revised sheet. | 2020-02-18
34 | LV drawings | J&A | Sheet LV 200,201,202,203,204,205 Note 2 states: Owner to provide new fixed camera,lens,housing as described by the specifications. Contractor to install camera and terminate CAT 6 cabling | 34: Correct. | 2020-02-18
35 | ACS questions | J&A | The specifications state that the ACS is to be integrated with the existing ACS. The manufacturer of the current ACS is not given can this be provided? | 35: Existing ACS manufacturer is Persona/DSX. | 2020-02-18
36 | VMS questions | J&A | The specifications state that the VMS is to be integrated with the existing VMS. The manufacturer of the current VMS is not given can this be provided? | 36: From our last call, the existing camera system on campus is in the process of being upgraded and they had not chosen which manufacturer they will be going with. Once they had decided, they were to let us know so we could work it into our specs. I have not heard if they had made a choice yet. I guess the answer would be TBD. The 2019 Design Guide doesn’t state a current manufacturer. The camera hardware is Bosch, but I’m not sure that they are using Bosch as the Video Management System. | 2020-02-18
37 | Section 064100 | MN | For the laminate materials in spec 064100 page 2, under 2.05 A. it calls for through color. 1.)Are they wanting color core material, if so that only comes in select colors and it cost a good bit more than standard laminate’s. 2.) And are they wanting melamine drawers because on page 3 section 2.07 Fabrication - Cabinets C. calls for dovetail joints which would be a solid wood drawer box design. | 1.)Provide color core material as specified.. 2.) Provide dovetail joints drawer boxes as specified. | 2020-02-18
38 | A900 | MN | Could you clarify what PL1 Is being used for, is it for the kitchen because PL.2 calls out the Resident Manager Apartment? | Finish Legend has been revised in Addendum #2 | 2020-02-18
ITEMS FOR ADDENDUM #3
2/18/20 Questions From Bidders and Drawings/Specification for ADDENDUM #3 |  |  |  |  | Date Competed
1 | Spec's | MN | Termite Treatment 31 31 16 was deleted from the updated spec's. Was this intentional? | Termite Treatment 31 31 16 will be removed from the TOC in Addendum #3 | 2020-02-19
2 | Spec's | MN | The previous manual included 32 31 31 Trash Dumpster Enclosure and the current manual does not. | 32 31 31 Trash Dumpster Enclosure will be removed from the TOC in Addendum #3 | 2020-02-19
3 | Storefront | MN/LAS | Aluminum storefronts are noted as having an anodized finish and also as having a painted finish, which will be required or will (2) finishes be required? | Base bid to be clear anodized for both. Alternate to be painted for both. See Addendum #3 for revisions. | 2020-02-19
4 | P200 | CMTA | See question No 5 that refers bidders to P200. There is no spec provided for the meter on P200 | Spec to be provided in Addendum #3 | 2020-02-21
5 | Plumbing Questions | CMTA | There is no detail and/or drawing for the intake and exhaust on the gas fired water heaters, please advise | Intake/exhaust shown on drawing M101 | 2020-02-21
6 | Section 00 24 13 | MN / LAS | BC-15 Aluminum Windows, doors and storefronts item 7F, include break-metal cover per detail 8/A822. On page A822 of the architectural drawing there is no detail 8/A822 | Note 7.f. on 00 24 13 - 69/80 should read "Include break-metal cover per detail 8/A820. | 2020-02-19
7 | Finishes | LAS | Units B1, B2, and C1 have RT1 for flooring. Is this a typo? Should it be LVT1? | Yes - flooring to be LVT1 | 2020-02-20
8 | Finishes | LAS | Units B1, B2, and C1 have RT1 for flooring. Is this a typo? Should it be LVT1? | Yes - flooring to be LVT1 | 2020-02-20
9 | S001 | THP | Note D. Concrete item 1a and 1b have (2) different drilled pier concrete psi's. Please clarify. | Drilled piers require 4,000 psi concrete. Delete drilled pier reference from Note D.1.a. | 2020-02-20
10 | Drawings and Spec | LAS | Clarify type(s) and locations of roller shades | Refer to Color Coded Plan (Attachments RS01 & RS02) for roller shade locations, as approved by NKU. | 2020-02-21
11 | Site Logistics Plan | MCC | Please confirm if BC-01 is to include all new pavement markings shown on C300 and temporary pavement markings per the Site Logistics Plan | BC-01 Shall provide all temporary pavement markings shown on the Site Logistics Plan. The painted crosswalk on Kenton Drive Shall be permanent and also be provided by the BC-01 contractor. | 2020-02-20
12 | Shaft openings at Level 2 | MN, LAS, THP | BC-01 item #17 sawcut for mechanical slab openings are only identified by (5) locations per S102, please clarify if these are the only saw cut locations or if every shaft opening 02 thru 05 labeled either by S102 note 10 or “MC” are to be saw cut | At all 5 locations noted by Coded Note 10 form the box-out, pour the concrete and 7 days later cut the metal decking. There will be concrete beam/slabs that form all openings at all MC locations. | 2020-02-20
13 | Section 00 24 13 | MCC | Please clarify what air barrier and flashing work are to be included with fiber cement siding, that aren’t already included in other exterior contractors work | The BC-07 provides; exterior sheathing, fluid applied membrane, insulation, and all “z” girts or metal shims require to provide a flush condition at the face of exterior insulation. The BC-01 shall provide any flashings, sub-girts, resilient furring channels required for a complete fiber cement system. The BC-15 contractor shall provide window flashings. | 2020-02-20
14 | Section 00 24 13 | MCC | Please clarify who provides the joint sealants, where shown, at intersection of fiber cement siding and other exterior systems (e.g. metal panels) | There will be many unique conditions where metal panel assemblies and fiber cement assemblies intersect and therefore the BC-01 and BC-14 shall both include joint sealants at the limits of there panels. Once shop manufactures shop drawings have be reviewed and approved the project will determine where sealants are necessary. | 2020-02-20
15 | Section 10 11 01 | LAS | Please clarify the VDB1, magnetic marker board sizes required in Study 101B and 101C, as the walls will not accommodate 10ft wide board typical elsewhere | 5’-0” x 5’-0” at 3’-0” AFF. An elevation will be included with addendum #3. | 2020-02-20
16 | Site Logistics Plan | MCC | Would it be acceptable to close Kenton Drive during work hours for the installation of the underground sanitary piping? | Yes, but this work will need to be coordinated with the CM and NKU so that it doesn't interfere with owner activities. | 2020-02-20
17 | Section 12 24 13 | NKU | Unfortunately, we do not carry the MechoShade brand, but we do carry comparable shades from Draper, SWFcontract, and Levolor. If it were up to me I’d go with Draper. They’re less expensive and made in Indiana. We can get them in 2 to 3 weeks, verses 4 to 6 weeks with Mecho. Would it be ok if I quoted you Draper? I can do a manual quote for the base and a motorized quote as an alternate. | No substitution request was submitted | 2020-02-21
18 | Section 10 14 00 | LAS | We have received inquiries from vendors who provide our current campus standard signage. As discussed earlier in the process and part of NKU design standards, interior room signage above and beyond code compliance will be owner furnished. Please confirm this is reflected in the specs and drawings. With that, any code related signage should aesthetically along, with code compliance, also conform to NKU Sign types standards/finishes. I’m attaching from our last project if this can be incorporated into the set/addendum | Signage has been revised. Refer to revised specification and Sheet A940. | 2020-02-21
19 | Section 10 14 00 | LAS | a. Cash allowance for signs – what is the cash allowance? | Allowance not needed. Refer to revised specification. | 2020-02-21
20 | Section 10 14 00 | LAS | b. Room and door signs – please confirm this is for code compliance, above and beyond interior room signage and wayfinding to be owner furnished, owner installed. | Signage has been revised. Refer to revised specification and Sheet A940. | 2020-02-21
21 | Section 10 14 00 | LAS | c. Emergency evacuation maps | Signage has been revised. Refer to revised specification and Sheet A940. | 2020-02-21
22 | Exterior Façade | MN | The plans are not clear on the Resilient channel in either the interior or exterior. On the exterior the plans call for 3/4" sub girt and RC Channel in the same locations. We would do RC1 channel, but not the sub girt. Please clarify. Also, neither material calls out a spacing. On the interior, their is no spacing requirements that I can find for the RC channel in the called for locations. Finally, can you please confirm the Drywall material needed on the exterior wall section? I can't find anything on the plans. | The "drywall" material needed on the outside. The reference to Resilient channels on the exterior side of walls in Details 7/A521, 2/A522, 4/A522 & 1/A523 have been changed to refer to Sub-girts. Details have been revised in Addendum #3. The Drywall sheathing mateial shall always be: "06 16 00.A1 Air and Water Resistive Sheathing Board." Details 5/A521 & 3/A522 have been revised in Addendum #3. Fluid applied membrane air barrier to be used on exterior of CMU walls. Detail 11/A521 has been revised in Addendum #3. | 2020-02-20
23 | A820 | LAS | Wood blocking is shown in jamb details on A820 but on A821 on the opposite side of the same opening there isn't blocking shown. Please clarify. | Wood blocking should be provided at all jamb conditions. | 2020-02-21
24 | A720 | MN / LAS | 1. Is the interior glass to be ¼” tempered or 1” insulated as shown on details 13 thru 15 on A720? 2. 2. Do the doors require mid-rails as per the specification 084113-6 2.03 E 2 c 3. 3. What type of film is to be applied to the interior glass (GL-3) per sheet A720 | 1. Interior glass should be 1/4" tempered. 2. Interior doors do not need a mid-rail. 3. Film is shown for coordination only and is intended to be a future project for NKU. | 2020-02-21
25 |  | LAS | Please provide a color for the solid surface tops | See item #17 from Addendum #2. | 2020-02-21
26 |  | MN / LAS | The longest warranty on anodized is only 10 year finish warranty? Per specification in 084113 Aluminum-framed entrances and storefronts it calls out 20 year finish warranty, as specified 2-coat 70% resin Knyar 500 can achieve a 20 year finish warranty. | base bid finish warranty to 10 years and alt bid warranty to 20 years. Revised spec sections 08 40 00 and 08 41 13 in Addendum #3 | 2020-02-20
27 | Exterior flashing and Trim | MN | It seems that the location of various types of flashing and trim ahs not been fully coordinated | Revised notes in details in several details on sheets A520, A521, A522, A523 & A731 | 2020-02-21
28 | G007 | MN | The 4J wall type on G007 does not include insulation but appears that is should be required. Please confirm that all 4J wall types shall receive insulation. | Yes - wall type 4J has been revised in Addendum #3 | 2020-02-21
29 | Section 05 12 00 | THP | Would non-AISC structural steel erectors be acceptable for fabrication/installation on this project? | The steel erector either has to be AISC Certified or they need to have an independent audit performed and submitted to ensure that they have an established QA/QC program comparable to the AISC program. See Spec Section 051200-1.4.C.3. | 2020-02-21
30 | Section 00 24 13 | MCC | Is it the responsibility of BC-01 or BC-15 contractor to finial clean windows? | Final window cleaning shall be provided by the BC-01 contractor. The BC-15 contractor shall remove all films, glue, caulk, and stickers prior to finial cleaning. | 2020-02-21
31 | Section 00 24 13 | MCC | Spec section 07 54 23 Thermoplastic Polyolefin Roofing is listed in BC-07 scope of work. Is this a mistake? | Yes | 2020-02-21
32 | Section 05 30 00 | MCC | Is metal decking included in BC-07? | No | 2020-02-21
33 | Section 00 24 13 | MCC | Who should remove the temporary sidewalks show to be installed by BC-01? | The BC-02 contractor shall remove the temporary sidewalks provided by others. This overrides the previous direction provided during the Pre-Bid Meeting Meetings. | 2020-02-21
34 | General | MCC | Is this project a OCIP or CCIP? | No. Subcontractor Default Insurance shall cover qualified bidders. This is not an added cost to bidders. | 2020-02-21
35 | General | MCC | Who provides the FRP around mop sinks? | All FRP is by the BC-01 subcontractor. | 2020-02-21
36
37
38
39
Kleingers
LAS
MN
THP
VLA
CMTA
J&A